# Lubrication of Landon Kingsway Free Fall Fire Valve

Step 1: Remove the lubricating screw from the end of the square shaft. (Important Ensure valve is in the open condition)

Step 2: Fill the reservoir inside the shaft with lubricant stick

Step 3: Replace the screw and tighten the screw until a definite increase in resistance is felt, inserting further lubricant as necessary.

Step 4: ‘Pump’ the valve lever up and down several times to ensure the valve is free-moving.

- Remove excess build-up of lubrication from valve when in the open position between the plug and valve body with rag.

- Use only a part or just one stick of lubrication at one time and test for leak tightness of system to atmosphere and pass seat (valve in close position)

- Always wear gloves